## Overview
FAULT TREE ANALYSIS — NUCLEAR POWER PLANT
Top-Level Event | Uncontrolled Reactor Core Damage (RCD)
Scope | Pressurised Water Reactor (PWR) — full plant
Analysis Method | Fault Tree Analysis (FTA) with Probabilistic Risk Assessment (PRA)
CDF Target | < 1×10⁻⁵ per reactor-year (NRC Reg. Guide 1.200)
Estimated CDF | ~1×10⁻⁵ to 1×10⁻⁶ per reactor-year
Standards Ref. | IEC 61513 ¦ IAEA SSR-2/1 ¦ NRC NUREG-1800
Date | 2026-02-22
Analyst | Claude Code / Agentic Skills FTA
Gate Legend
OR gate (∨) | Top event occurs if ANY one of the sub-events occurs
AND gate (∧) | Top event occurs only if ALL sub-events occur simultaneously
Basic event ○ | Root cause — no further decomposition required
Intermediate | Intermediate event — decomposed further into sub-events

## Fault Tree Structure
Fault Tree Structure — Nuclear Power Plant
Level | Event ID | Event Name | Event Type | Gate | Parent Event ID | Description
0 | TOP | Uncontrolled Reactor Core Damage | TOP EVENT | AND | — | Primary undesired outcome: fuel integrity lost, radioactive release possible
1 | LHR | Loss of Heat Removal | Intermediate | OR | TOP | Heat cannot be removed from the core
1 | RCF | Reactivity Control Failure | Intermediate | OR | TOP | Reactor cannot be shut down when required
2 | LOCA | Loss of Coolant Accident | Intermediate | OR | LHR | Coolant escapes the primary circuit
2 | DHR | Decay Heat Removal Failure | Intermediate | AND | LHR | All emergency core cooling trains fail
2 | SCRAM | Control Rod SCRAM Failure | Intermediate | AND | RCF | Control rods fail to insert on demand
2 | BORON | Emergency Boration Failure | Intermediate | OR | RCF | Boron injection system fails
3 | E01 | Large-break pipe rupture | Basic Event | — | LOCA | Primary coolant pipe guillotine failure
3 | E02 | Small-break LOCA (seal/valve) | Basic Event | — | LOCA | Coolant pump seal or small valve leaks
3 | E03 | RPV failure | Basic Event | — | LOCA | Reactor Pressure Vessel integrity loss
3 | E04 | Steam generator tube rupture | Basic Event | — | LOCA | SGTR causing primary-to-secondary leakage
3 | E05 | HP injection pump fails | Basic Event | — | DHR | High-pressure ECCS pump fails on demand
3 | E06 | LP injection pump fails | Basic Event | — | DHR | Low-pressure ECCS pump fails on demand
3 | E07 | Passive accumulator fails | Basic Event | — | DHR | Nitrogen-driven accumulator fails to inject
3 | E08 | Control rod mechanically stuck | Basic Event | — | SCRAM | Rod distortion/swelling prevents insertion
3 | SIG | SCRAM Signal Not Generated | Intermediate | AND | SCRAM | Automatic and manual SCRAM both unavailable
3 | E11 | Boron pump fails to start | Basic Event | — | BORON | Motor or mechanical failure of boron pump
3 | E12 | Boration supply valve fails closed | Basic Event | — | BORON | Valve fails in closed position
3 | E13 | Wrong boron concentration | Basic Event | — | BORON | Dilution error or incorrect tank fill
4 | E09 | Neutron flux sensor failure | Basic Event | — | SIG | Instrumentation fails to detect power excursion
4 | E10 | Operator fails manual SCRAM | Basic Event | — | SIG | Human error: SCRAM not initiated manually

## Probability Analysis
Probability Analysis — Basic & Intermediate Events
Event ID | Event Name | Failure Rate | Unit | Gate to Parent | Propagated P | Notes
E01 | Large-break pipe rupture | 1×10⁻⁴ | /year | OR (LOCA) | 1×10⁻⁴ | Per NUREG-1829 pipe failure rates
E02 | Small-break LOCA (seal/valve) | 5×10⁻³ | /year | OR (LOCA) | 5×10⁻³ | Most frequent LOCA initiator
E03 | RPV failure | 1×10⁻⁶ | /year | OR (LOCA) | 1×10⁻⁶ | Includes PTS screening criteria
E04 | Steam generator tube rupture | 5×10⁻³ | /year | OR (LOCA) | 5×10⁻³ | Per EPRI TR-107396
LOCA | LOCA (combined OR) | — | — | OR → LHR | ~1×10⁻² | 1−∏(1−Pᵢ) ≈ sum for small P
E05 | HP injection pump fails | 1×10⁻³ | /demand | AND (DHR) | — | Single train; 3 trains total
E06 | LP injection pump fails | 1×10⁻³ | /demand | AND (DHR) | — | Single train; 3 trains total
E07 | Passive accumulator fails | 1×10⁻⁴ | /demand | AND (DHR) | — | Nitrogen-pressurised; passive
DHR | Decay Heat Removal Failure (AND) | — | — | OR → LHR | 1×10⁻¹⁰ | 1e-3 × 1e-3 × 1e-4 = 1e-10
E08 | Control rod mechanically stuck | 1×10⁻⁴ | /demand | AND (SCRAM) | — | Rod drop surveillance data
E09 | Neutron flux sensor failure | 1×10⁻² | /year | AND (SIG) | — | Redundant channels reduce system P
E10 | Operator fails manual SCRAM | 1×10⁻³ | /demand | AND (SIG) | — | Per HRA THERP methodology
SIG | SCRAM signal not generated (AND) | — | — | AND→SCRAM | 1×10⁻⁵ | 1e-2 × 1e-3 = 1e-5
SCRAM | Control Rod SCRAM Failure (AND) | — | — | OR → RCF | 1×10⁻⁹ | 1e-4 × 1e-5 = 1e-9
E11 | Boron pump fails to start | 5×10⁻⁴ | /demand | OR (BORON) | 5×10⁻⁴ | Redundant pump available
E12 | Boration valve fails closed | 1×10⁻³ | /demand | OR (BORON) | 1×10⁻³ | Normally-open valve failure
E13 | Wrong boron concentration | 1×10⁻³ | /demand | OR (BORON) | 1×10⁻³ | Chemistry surveillance reduces risk
BORON | Emergency Boration Failure (OR) | — | — | OR → RCF | ~2.5×10⁻³ | Combined OR of E11/E12/E13
RCF | Reactivity Control Failure (OR) | — | — | AND → TOP | ~2.5×10⁻³ | OR of SCRAM + BORON ≈ BORON
LHR | Loss of Heat Removal (OR) | — | — | AND → TOP | ~1×10⁻² | OR of LOCA + DHR ≈ LOCA
TOP | Core Damage (AND of LHR + RCF) | — | — | — | ~2.5×10⁻⁵ | 1e-2 × 2.5e-3 = 2.5e-5/yr CDF

## Minimal Cut Sets
Minimal Cut Sets (MCS) — Critical Failure Paths
MCS ID | Events Required | No. of Events | Combined Probability | Risk Level | Description
MCS-1 | Small-break LOCA (E02) + HP fail (E05) + LP fail (E06) + Accumulator fail (E07) | 4 | ~5×10⁻¹³ | Very Low | Full ECCS failure following LOCA; deep defence-in-depth
MCS-2 | Large-break LOCA (E01) + HP fail (E05) + LP fail (E06) + Accumulator fail (E07) | 4 | ~1×10⁻¹⁰ | Low | Guillotine break with total ECCS failure
MCS-3 | Rod stuck (E08) + Sensor fail (E09) + Operator error (E10) + any LOCA | 4 | ~5×10⁻¹³ | Very Low | SCRAM failure combined with LOCA initiator
MCS-4 | Rod stuck (E08) + Boron valve fails (E12) + any LOCA | 3 | ~5×10⁻⁷ | Moderate | Fewer redundant barriers; boration is last line
MCS-5 | RPV failure (E03) | 1 | ~1×10⁻⁶ | Moderate | Single basic event; bypasses all ECCS — highest structural priority
MCS-6 | SGTR (E04) + all ECCS trains fail | 4 | ~5×10⁻¹³ | Very Low | Steam generator tube rupture with ECCS unavailability
MCS-7 | Wrong boron concentration (E13) + rod stuck (E08) + any LOCA | 3 | ~5×10⁻⁸ | Moderate | Chemistry error combined with mechanical SCRAM failure

## Corrective Actions
Corrective Actions & Risk Mitigation
Event ID | Basic Event | Probability | Priority | Prevention | Detection | Mitigation | Standard Reference
E02 | Small-break LOCA | 5×10⁻³/yr | High | Seal inspection program, leak-before-break design | Coolant pressure/flow alarms, continuous leakage monitoring | Emergency boration, ECCS actuation procedures | IAEA SSR-2/1 §5.4
E01 | Large-break pipe rupture | 1×10⁻⁴/yr | High | In-service inspection (ISI), stress corrosion monitoring | Break detection sensors, LOCA alarms | ECCS high-pressure injection, operator EOPs | NRC Reg. Guide 1.200
E03 | RPV failure | 1×10⁻⁶/yr | High | Fracture toughness surveillance, PTS thermal limits | RPV integrity monitoring, thermal shock screening | Depressurisation procedures, boration | ASME Code Case N-640
E04 | SGTR | 5×10⁻³/yr | High | Eddy current testing of tubes, anti-vibration bars | Primary-to-secondary leak monitors, radiation alarms | Steam generator isolation, controlled cooldown | EPRI TR-107396
E11 | Boron pump fails | 5×10⁻⁴/dem | High | Redundant pump train, monthly functional tests | Pump start confirmation, flow indicators | Backup boration tank, gravity feed path | IEC 61513 §8.3
E08 | Control rod stuck | 1×10⁻⁴/dem | Medium | Rod drop time testing, friction surveillance | Rod position indication, drop time alarms | Alternate shutdown via emergency boration | IAEA SSR-2/1 §6.2
E05 | HP injection pump fails | 1×10⁻³/dem | Medium | Preventive maintenance, redundant trains (3+1) | Auto-test on standby, flow rate indicators | Alternate injection path, cross-connect valve | IEC 61513 §9.1
E06 | LP injection pump fails | 1×10⁻³/dem | Medium | Scheduled overhaul, staggered maintenance | Standby run tests, vibration monitoring | Gravity-feed injection mode | IEC 61513 §9.1
E10 | Operator fails manual SCRAM | 1×10⁻³/dem | Medium | Simulator training (quarterly), written EOPs | Annunciator panels, automatic SCRAM logic backup | Automatic backup SCRAM on high neutron flux | NUREG-1792
E12 | Boration valve fails closed | 1×10⁻³/dem | Medium | Normally-open design, valve position indication | Valve position monitoring, periodic stroke test | Manual operator action, alternate flow path | IEC 61513 §8.3
E07 | Accumulator fails | 1×10⁻⁴/dem | Low | Periodic nitrogen pressure checks, seal inspection | Pressure indicators on accumulator tanks | Alternate low-pressure injection | IAEA SSR-2/1 §5.6
E09 | Neutron flux sensor failure | 1×10⁻²/yr | Low | Redundant detector channels (4-channel voting) | Channel calibration checks, deviation alarms | Manual SCRAM initiated by operator | IEC 61513 §10.2
E13 | Wrong boron concentration | 1×10⁻³/dem | Low | Boron concentration sampling, two-person verification | Boric acid analysers, continuous conductivity monitors | Dilute and re-inject, alternate tank | ASTM D1838